## Slide 1
Port Czystej Energii Sp. z o.o. biuro@portczystejenergii.pl www.portczystejenergii.pl
CONSTRUCTION OF THE THERMAL WASTE TREATMENT PLANT IN GDAŃSK

## Slide 2
WHY DO WE NEED A MODERN WASTE INCINERATION PLANT?
increased quantity of waste generated
lack of other possibility to process non-recyclable waste (the so called energy fraction from municipal waste)
the need to stabilise prices for energy fraction management
landfilling of energy fraction prohibited
less landfill space/landfill limit up to 10% in 2030
MUNICIPAL WASTE MANAGEMENT SYSTEM IN gdańsk

## Slide 3: Waste hierarchy
The least desirable option
The most desirable option
WASTE
Prevention
Minimisation
Reuse
Recycling
Energy recovery
Landfill

## Slide 4
Quantity of waste generated by 1 resident of Gdańsk within a year. Is that a lot?

## Slide 5
Chart: 
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
PSZOK | 1463.324 | 1448.658 | 1650.182 | 1921.215 | 2500.099 | 3060.181 | 4726.237
raw materials | 5326.83 | 5901.74 | 6150.54 | 7797.7 | 9837.56 | 18793.05 | 25789.77
bio | 9759.98 | 20625.58 | 23529.07 | 27705.56 | 29214.34 | 30564.52 | 31410.5
residual/mixed | 128062.094 | 126644.148 | 129058.181 | 135476.8 | 134807.31 | 127058.84 | 122471.818
other | 5338.613 | 6538.981 | 7345.237 | 8613.636 | 9497.826 | 9936.205 | 11385.414
Notes: Prawym – edytuj dane

## Slide 6
Chart: wet/bio-waste
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
odpady mokre/bio | 2834.2 | 9759.98 | 20625.58 | 23529.07 | 27705.56 | 29214.34 | 30564.52 | 31410.5

## Slide 7
Recycling rates of the City of Gdańsk
- reached and planned
As you can see the obligation of selective waste collection by residents is not a remedy for the municipal waste management system in Poland
rate reached
rate required

## Slide 8
Costs of the municipal waste management system in Gdańsk (PLN)

## Slide 9
The need to meet the growing requirements related to waste management
  Reduction of landfilling of biodegradable waste by 65% compared to 1995
  Recycling and preparation for reuse of at least 50% municipal waste
  Reaching the municipal waste recycling target of 65%
  Reduction of waste landfilling up to max. 10%
  Llandfilling of waste with a TOC content > 5% and a combustion heat > 6 MJ/kg prohibited
2016
2020
2035
Prohibitions and requirements

## Slide 11: ZTPO – a thermal waste treatment plant implementing the objectives of the circular economy
Notes: Osobno tez

## Slide 12
SORTOWNIA
Municipal installations ZZO
INCINERATION PLANT
HEAT
SLAG
construction or
landfilling
ELECTRICITY
pre RDF
Comminuted large-size waste
Combustible ballast from sorting plant
SUBSCREEN FRACTION
Future with an operating incineration plant
160 Mg/year
Energy fraction ≥ 11MJ/kg
Projected quantity and composition of energy fraction
Energy fraction
(non-recyclable waste)

## Slide 13
Increased costs of energy fraction management in the years 2018/2020 – 35 million PLN
Costs of energy fraction management in ZTPO – based on the current financial model of the project (2024-2048)
Forecast based on quantitative data of individual waste streams in ZU in 2019
Costs based on ZU tenders and current environmental fees for landfilling
Projected impact of ZTPO on the energy fraction management costs (theoretical assumptions) on the example of ZU Sp. z o.o.

## Slide 14: Development of a heating network in Gdańsk
Total power in the heating network
of the GPEC Group
1138 MW
Chart: 
Chart: 
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
MW | 42 | 37 | 47 | 42 | 53 | 51 | 41 | 36
NEW CONNECTIONS 2014-2020 AND PLANNED IN 2021
Number of residents connected
to the GPEC network
> 400 000
PLAN
[MW]
Investments in the development of the heating network in 2019
49,7 million

## Slide 15: ZTPO construction financial structure
Chart: 
Chart: 
| Dofinansowanie | Pożyczka
koszty | 270696804.83 | 296166840.29

## Slide 16: Project of connecting ZTPO to the municipal heating network - milestones
TO DO
Preparation of projects and obtaining construction permits (2021-2022)
Preparation of documents for tender and selection of contractors (2021-2022)
Construction of heating connection and PBS (2021-2023) 1,8 km of a new network in Gdańsk, 24 million PLN investment value
Heat supply to ZTPOK (2023/2024)
COMPLETED
Issue of Technical Conditions for connecting ZTPO to the municipal heating network
Detailed analysis of the ZTPO impact on the operation of MHN
The concept of connection routes and technological diagrams of the pressure boosting station (PBS)
Conclusion of the contract for the connection of heat source to MHN (14.08.2019)
Preparation of technical specifications (TS) for the connection project and PBS
Commencement of the project phase for the construction of the heating connection between ZTPOK and MHN and the construction of PBS

## Slide 17: ZTPO impact on the heating network
The production of heat energy in ZTPO – 509TJ/year - the heat will be supplied to the district heating network GPEC
Heat power in cogeneration – 45 MWt (out of 11 MWe) - it will be on average 6% of the demand for heat and hot water in Gdańsk
The areas of Gdańsk co-supplied by Port Czystej Energii vary depending on the season:
In the winter 46,2 km of the network will co-supply the following districts with heat and hot water: south part of Jasień, Ujeścisko-Łostowice, Kolbudy –north-east part – about 19 thousand households
In the summer over 160 km of the network will additionally co-supply the following districts: Chełm, Wzgórze Mickiewicza, Siedlce, Suchanino, Wrzeszcz Górny – south part, Piecki-Migowo – south part, Aniołki – south part – about 70 thousand households

## Slide 18: Post-production waste management
SLAG
The slag management lies with the Ordering Party, the entity responsible for the slag management/collection will be selected by tender;
The amount of slag is about 20-25% of the waste stream burnt on the grate;
The slag valorisation segment will work 8 hours a day, 5 days a week
The slag will be managed depending on current capabilities:
  disposed of and used e.g. in the construction sector, for road construction, etc.
  landfilled
ASH
The ash management from the exhaust gas treatment system lies with the Contractor and he is obliged to manage the waste outside the incineration plant, i.e. in the inactive mines
The amount of ash is about 4,5% of the waste stream burnt on the grate
20-25%
5%

## Slide 19: Advantages of ZTPO
How the incineration plant will influence the costs of the waste management system:
Lower prices for energy fraction management
Predictable prices for thermal waste treatment
Reduction of waste landfill fees
Income from the sale of electricity and heat from waste will lower the gate fee
Non-financial advantages of the incineration plant:
Management of non-recyclable waste
Management of the troublesome subscreen fraction
Reduction of the amount of waste collected in landfills
Use of waste for diversifying heat and electricity sources
Environmental effects: reduction of pollutant air emissions, reduction of fossil fuel use
Annual production of electricity generated in the incineration plant will be enough to power the entire tram fleet in Gdańsk for 3,5 years
1 year
3,5 years

## Slide 20: Rainwater – types of sewage systems
Rainwater and meltwater will be directed to the rainwater drainage system which will consist of 2 networks:
“clean”
  - Collection of rainwater or meltwater from roofs of buildings and facilities.
  Rainwater from roofs will be directed to a retention tank with a capacity of 140 m3, and subsequently used on an ongoing basis e.g. for cleaning floors, watering plants or depending on the possibilities for technological purposes.
“dirty”
  - Collection of other rainwater or meltwater, e.g. from streets and squares.

## Slide 21: Rainwater - devices
Devices for the collection, treatment and drainage of rainwater and meltwater include:
Retention tank for rainwater from roofs,
Retention tank for rainwater from streets and pavements together with a drain controller,
Oil derivatives separator integrated with the tank,
Rain gardens,
Reed bed,
Outlet to the Kozacki Stream.

## Slide 22: Climate protection and rainwater management
Devices for retention of rainwater or meltwater from sealed areas will include four rain gardens with the following capacities:
179,63 m3 –eastern rain garden
78,8 m3 and 60 m3 –central rain gardens
203 m3 – western rain garden – car park
2%
5 cm rock (3-6 cm fraction)
40 cm mixture of earth and sand (1:3)
10 cm sand
20 cm gravel
pcv foil
Emergency overflow
Rainwater from ZTPO
EXCESS OF WATER
Kozacki stream
pebbles
Notes: Urządzeniami służącymi do retencjonowania wód opadowych lub roztopowych z terenów uszczelnionych będą ogrody deszczowe o pojemnościach:
179,63 m3 – ogród deszczowy wschód
78,8 m3 i 60 m3 – ogrody deszczowe środek
203 m3 – ogród deszczowy zachód - parking
Zadaniem czterech ogrodów deszczowych jest zbieranie i wykorzystywanie wody opadowej z pobliskich terenów. Zaproponowano tu tzw. „mokre” ogrody deszczowe, które posiadają szczelne dno wykonane z foli pcv. Ogrody zbudowane są bezpośrednio w gruncie. Warstwę uszczelniającą – folię pcv należy pokryć 20 cm warstwą żwiru, której zadaniem jest filtrowanie wody a na nią 10 cm warstwę czystego, płukanego piasku. Następnie należy ułożyć warstwę wegetacyjną dla roślin złożoną z mieszanki żyznej ziemi z piaskiem. Ziemię należy wymieszać w stosunku 1:3 – jedną część ziemi żyznej należy wymieszać z trzema częściami piasku. W celu zabezpieczenia przed wymywaniem części żyznych gleby i erozją wodną należy na warstwę wegetacyjną wyłożyć 5 cm warstwę kamieni o frakcji 3-6 cm. Dodatkowo w miejscach spływu wody wartkim strumieniem do ogrodów deszczowych należy układać otoczaki, które będą chroniły ogrody przed erozją wodną. Ogrody wyposażone będą w wpusty awaryjne, np. grzybkowe, służące do odprowadzania nadmiaru wody.
W ogrodach deszczowych należy sadzić rośliny hydrofitowe. Są to rośliny, które znoszą okres suszy oraz są odporne na zalewanie, a dodatkowo oczyszczają wodę. Aby uniknąć corocznych nasadzeń mogących poruszyć warstwy drenujące, do projektowanych ogrodów zastosowano byliny – rośliny wieloletnie, występujące naturalnie w polskich zbiorowiskach roślinnych, występujących w ekosystemach nadwodnych i okresowo zalewanych. Proponowane gatunki roślin to m.in. krwawnica pospolita (Lythrum salicaria), mozga trzcinowata (Phalaris arundinacea) i żabieniec babka wodna (Alisma plantago-aquatica).

## Slide 23: Sewage – directed to the district sewage system
Domestic sewage will be discharged to the district sewage system by sewage installation.
Industrial waste water produced in the regeneration process will be stored in a special tank located in the water treatment plant. After their neutralisation they will be reused for technological purposes, e.g. for refilling the slag trap. The excessive neutralised waste water will be discharged to the sanitary sewage system.
TYPES OF SEWAGE | Quantity of sewage discharged |  | 
 | per hour | per day | per year
 | m3/h | m3/d | m3/year
Industrial waste water – waste water from periodic cleaning of the unloading hall floor and from the water treatment plant | 5,0 | 30,0 | 10 950
Domestic sewage | 0,4 | 6,34 | 2 314
IN TOTAL | 5,4 | 36,34 | 13 264
Notes: Parametry odprowadzanych ścieków będą spełniać wymogi określone w Rozporządzeniu Ministra Budownictwa z dnia 14 lipca 2006 r. w sprawie sposobu realizacji obowiązków dostawców ścieków przemysłowych oraz warunków wprowadzania ścieków do urządzeń kanalizacyjnych (t.j. Dz.U.2016 poz. 1757) oraz wymogi określne przez odbiorcę. Ww. ilości oraz rodzaje ścieków zostały podane w dokumentacji technicznej, która została pozytywnie uzgodniona przez Gdańską Infrastrukturę Wodociągowo – Kanalizacyjną Sp. z o.o. (GIWK). W/w ścieki będą odprowadzane do kanalizacji miejskiej poprzez instalację kanalizacyjną należącą do Zakładu Utylizacyjnego.

## Slide 24: Process water Sewage pre-treatment
All works related to the separator cleaning will be subcontracted to external companies. Waste will not be stored on site. Directly after its production it will be removed from the site with a special means of transport by a company with appropriate authorisation to manage this type of waste. It is intended for further disposal.
The following sewage pre-treatment plants were designed:
a sewage pre-treatment plant with a laboratory – pre-treated sewage will be discharged to the sanitary sewage system
a pre-treatment plant for rainwater and meltwater from streets and squares – consists of an oil derivatives separator integrated with a tank
a pre-treatment plant for waste water from periodic cleaning of the unloading hall floor – consists of an oil derivatives separator integrated with a tank
neutralisation of waste water from the water treatment plant – waste water produced in the regeneration process will be stored in a special tank located in the water treatment plant. After their neutralisation they will be reused for technological processes, e.g. for refilling the slag trap. The excessive neutralised waste water will be discharged to the sanitary sewage system. Waste from the neutralisation of waste water from the water treatment plant are not expected to occur.
a pre-treatment plant for rainwater and meltwater from oil drip pans - consists of an oil derivatives separator
a sewage disposal system consists of pumps and tanks for sewage from a bunker for storing waste intended for thermal treatment. Two tanks were designed with a capacity of 1 m3 each. They will be emptied by a septic tanker and exported for disposal by a company with appropriate authorisation to manage or dispose of this type of sewage.
Notes: Na terenie Zakładu Termicznego Przekształcania Odpadów Komunalnych (ZTPOK) zaprojektowane zostały następujące podczyszczalnie ścieków:
podczyszczalnia ścieków z laboratorium. Podczyszczone ścieki będą odprowadzane do kanalizacji sanitarnej.
Szacunkowa ilość odpadów średnio w skali roku ok. 0,25 Mg.
Szacowana ilość ścieków z laboratorium to ok 0,025 m3/d.
podczyszczalnia wód opadowych i roztopowych z dróg i placów, składająca się z separatora substancji ropopochodnych zintegrowanego z osadnikiem
Szacunkowa ilość odpadów średnio w skali roku ok. 4 Mg.
podczyszczalnia ścieków z okresowego mycia posadzki hali wyładunkowej, składająca się z separatora substancji ropopochodnych zintegrowanego z osadnikiem – 2500 dm3.
Odpad stanowi w większości piasek oraz osady, szlamy zanieczyszczone substancjami ropopochodnymi.
Szacunkowa ilość odpadów średnio w skali roku ok. 1 Mg.
neutralizacja ścieków ze stacji uzdatniania wody –ścieki wytwarzane w procesie regeneracji będą przechowywane w dedykowanym zbiorniku znajdującym się w pomieszczeniu stacji uzdatniania wody. Gdy ścieki zostaną zneutralizowane, zostaną użyte do ponownego wykorzystania do celów technologicznych, np. do uzupełniania strat w odżużlaczu. Nadmiar zneutralizowanych ścieków będzie odprowadzany do kanalizacji sanitarnej. Nie przewiduje się powstawania odpadów z neutralizacji ścieków ze stacji uzdatniania wody.
podczyszczalnia wód opadowych i roztopowych z tacy rozładunkowej oleju, składająca się z separatora substancji ropopochodnych
Szacunkowa ilość odpadów średnio w skali roku ok. 0,15 Mg.

## Slide 25: Process water Elements of water and sewage system
Underground process water tanks:
Water collected in process water tanks will be reused for the following purposes:
DEMINERALISED WATER TANKS
(a total capacity of 80m3)
– boiler refilling, SNCR system,
boiler cleaning system, limewater preparation
INDUSTRIAL WATER TANKS
(40m3)
- limewater preparation, water refilling in the slag trap.
Storage of water from boiler desalination and blowdown and water from exhaust gas treatment system (condensate). The contents of the tank will be directed to the cleaning process for further use
Process tank no. 1
(160m3)
Temporary storage of water from exhaust gas treatment system (condensate)
Process tank no. 2
(35m3)
Process tank no. 3
(50m3)
Storage of waste water from floor cleaning, emergency emptying of a slag trap, emptying of the limewater tank and exhaust gas condenser, water from slag processing and storage building. Waste water, if possible, will be reused in the slag trap. The excess will be collected by a company with appropriate authorisation.

## Slide 26
LOWER POLLUTANT AIR EMISSION LIMITS
EXTENDING THE SCOPE OF CONTINUOUS MONITORING OF POLLUTANT AIR EMISSIONS
The exhaust gas analyser (CEMS) will be extended with a continuous measurement of the mercury and ammonia content in exhaust gases
 | Adjustment by:
Ash | – increasing the efficiency of the existing system (bag filter)
Acidic pollutants (sulphur oxides, hydrogen chloride) | – increasing the efficiency of the existing systems (limestone reagent dosing, bag filter) – adding a new magnesium reagent injection system
Dioxins, furans, heavy metals | – increasing the efficiency of the existing system (activated charcoal dosing into the exhaust gases, selection of a more suitable type of activated charcoal)
Nitrogen oxides and ammonia | - Adding a new selective catalytic reduction system (SCR)
New BAT conclusions – conclusions for ZTPO
Notes: Decyzja wykonawcza Komisji Europejskiej zawierająca nowe konkluzje najlepszych dostępnych technik (tzw. BAT – Best Available Techniques) dla instalacji termicznego przekształcania odpadów została opublikowana w grudniu 2019 r.
Wynika z niej konieczność dostosowania ZTPO do nowych wymagań, przede wszystkim w zakresie dopuszczalnych limitów emisji substancji do atmosfery.
Zmiany projektowe ZTPO mające na celu dostosowanie go do nowych wymagań realizowane są na dwa sposoby:
Zwiększenie wydajności i skuteczności istniejących systemów oczyszczania spalin. Ten sposób ma zastosowanie m.in.
  dla pyłu poprzez zwiększenie skuteczności filtra workowego,
  dla kwaśnych zanieczyszczeń (tlenki siarki, chlorowodór) poprzez zwiększenie wydajności dozowania reagenta wapiennego do spalin,
  dla dioksyn, furanów i metali ciężkich poprzez zwiększenie wydajności układu dozowania węgla aktywnego do spalin.
Dodanie nowych urządzeń oczyszczających spaliny. Ten sposób ma zastosowanie m.in.
  dla tlenków azotu i amoniaku poprzez dodanie katalitycznego systemu odazotowania spalin (SCR),
  dla kwaśnych zanieczyszczeń poprzez dodanie układu wtrysku reagenta magnezowego do kotła.
Dodatkowo, wprowadzona została konieczność ciągłego pomiaru zawartości rtęci i amoniaku w spalinach wyprowadzanych przez komin. W celu spełniania tego wymogu, zastosowany analizator spalin (CEMS) zostanie rozbudowany o pomiar tych dwóch substancji.
Na czerwono zaznaczone są nowe układy – dozowanie reagenta magnezowego do kotła (po lewej stronie) i układ katalitycznego odazotowania spalin SCR (po prawej stronie).
Na żółto zaznaczone są istniejące układy, których skuteczność zostanie podniesiona – układy dozowania reagenta wapiennego i węgla aktywnego oraz filtr workowy.
Planowane zmiany zapewnią pełną zgodność rozwiązań technologicznych ZTPO z najnowszymi europejskimi wymaganiami oraz zagwarantują spełnienie nowych, bardziej rygorystycznych limitów emisji substancji do powietrza, które będą obowiązywały ZTPO w momencie jego uruchomienia, co będzie miało pozytywny wpływ na środowisko i mieszkańców.

## Slide 27: Changes in the exhaust gas treatment plant ZTPO
BUNKER
BOILER
GRATE
EXHAUST GAS TREATMENT PLANT
CHIMNEY

## Slide 28: Environmental effects of the ZTPO commissioning
Reduction of CO2 emissions (ZTPO cogeneration)
CO2-emissions are by 164 000 Mg per year lower compared to the separate production of electricity and heat based on coal.
Reduction of fossil fuel use
Saving of 52 800 Mg hard coal and 47 200 Mg lignite per year (estimation)
Reduction of the quantity of municipal waste landfilled
– reduction of landfill gas emission by 1 840 000 m3 per year
Reduction of emission
1
2
3
4
Chart: 
| NOx | SOx | Pyły
Incineration plant | 100 | 30 | 5
coal power plants | 300 | 400 | 30
mg/Nm3

## Slide 29
 | 2020 |  |  |  |  |  |  |  |  |  |  |  | 2021 |  |  |  |  |  |  |  |  |  |  |  | 2022 |  |  |  |  |  |  |  |  |  |  |  | 2023 |  |  |  |  |  |  |  |  |  |  | 
 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Land exchange |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Bunker and unloading hall |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Boiler house |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Exhaust gas treatment building |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Turbine and generator building/Machine room |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Administrative building |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Waste sample preparation building |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Chimney |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Boiler, grate, drum |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Overhead heating chamber |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Turbine and turbo-generator |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Slag pre-stabilisation building |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Slag trap |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Heating connection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Finishing works, performance of outdoor installations, roads and land development |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Commissioning |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Use permit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Milestones of the ZTPO construction

## Slide 30
ZTPO construction schedule
VII
Commencement of earthworks
V
Commencement of start-up works
XII
Commencement of construction works (other than earthworks)
X/XI
Commissioning
VII
Assembly of installations and technological devices
Land exchange
2020
2021
2022
2023